Annexure - C

Project Completion Report for Grid-Connected Rooftop

| Financial year: | 2025-26 |  |  |
| --- | --- | --- | --- |
| Sanction Letter No. : | NP-APEPD24-002209805 |  |  |
| Proposal Title : | Domestic Roof Top Solar |  |  |
| Installed by agency : | Immadi Srinivasarao |  |  |
| Title of the Project: | 5kw Roof Top Solar | SPV Capacity (kWp): | 4.95KWp |
| Category of the organization/ beneficiary: | BRIHASPATHI TECHNOLOGIES LIMITED | Name of the contact person: | Ramu T |
| Address of contact person: | S/O, Nageswara Rao, Dwaraka Tirumala (A2,b2)dwaraka Tirumala (A2,b2), Eluru Dist, Andhra Pradesh State-534426, |  |  |
| State: | Andhra Pradesh | District/ City: | Eluru |
| Mobile: | 9848966166 | Email: |  |
| Aadhaar Card Number (For Residential) | 5137 4807 2949 | Latitude: | 16.953656 |
|  |  | Longitude: | 81.255313 |
| DISCOM | APEPDCL | Sanction Load | 5kw |
| CA No. |  |  |  |

| Technology Description & System Design/Specification |  |  |  |
| --- | --- | --- | --- |
| (Compliance to BIS/ IEC Standards is mandatory) |  |  |  |
| 1. Solar PV Module: |  |  |  |
| Power of each PV Module / Nos.(Wp)* / Make | 535WP |  |  |
| Cumulative Capacity of Modules (kWp): | 5.35 kWp |  |  |
| Solar cell technology: | Mono Crystalline | Tilt Angle of Modules: | 12 |
| Module efficiency (in %) : | 20.71 | Azimuth | 0 |
| Indigenous or imported (Cell) | indigenous | RFID passed inside or outside: | inside |
| Indigenous or imported (Module) | Indigenous | * Supported by Appropriate documentation |  |
| 2. Inverters: |  |  |  |
| Type of inverter : | Grid Tie Inverter |  |  |
| Power of each PCU/Nos. of inverters (KVA)* /Make | 5KW |  |  |
| Capacity/Power of PCU/inverters (KVA) : | 5kw | Type of Charge Controller /MPPT | One MPPT |
| Inverter efficiency (in %) | 97.1 % |  |  |
| Grid connectivity level phase | Single Phase | Grid connectivity level Voltage | 220 V |

| 3. Mounting Structures |  |  |  |
| --- | --- | --- | --- |
| Type | Fixed | Surface Finish | Aluminum |
| Material | Aluminum | Wind Speed Tolerance | 180kmph |
| 4. Cables: |  |  |  |
| DC Cable Make | Poly Cab | Size | 6 Sqmm |
| AC Cable Make (Inverter to ACDB) | Poly Cab | Size | 4C X 10 sQMM |
| AC Cable Make (ACDB to Electric Panel) | Poly Cab | Size | 4C X 10 sQMM |
| Conductor | Multi Standard Cable | Insulation/ sheath | PVC / XLPE |
| 5. JUNCTION BOX & DISTRIBUTION BOARDS |  |  |  |
| ACDB | L& T | Nos. | 1 |
| DCDB | Elmex | Nos. | 1 |
| 6. EARTHING & LIGHTNING PROTECTION |  |  |  |
| EQUIPMENT EARTHING |  |  |  |
| AC (Nos.) | 1 | Earth Resistance | 5.2 Ohms |
| DC (Nos.) | 1 | Earth Resistance | 5.8 Ohms |
| LIGHTNING ARRESTORS (LA) |  |  |  |
| Type | Globe |  |  |
| LA (Nos.) | 1 | Earth Resistance | 5.5 Ohms |
| 7. Online Monitoring Mechanism: |  |  |  |
| Web Portal : | https://www.semsportal.com/home/login |  |  |
| USER ID : | ramu@brihaspathi.com | Password: | Solar@123 |
| 8. Weather monitoring: |  |  |  |
| Solar Irradiance (Pyranomerter - Class IInd or better) | NA | Temperature | Ambient & Module |
| Wind speed sensor | NA |  | NA |
| 9. Fire Fighting Device / System | NA |  |  |
| 10. Danger Board | Available |  |  |

Date: 27.05.2025	(Signature of Vendor)

With Stamp

Annex:

1. Copy of System test & Earth test reports(annexed)

Commissioning Test Report: Solar Project ……. kW

Inverter Testing (DC) Side: Nos. of Inverter 01 Nos.

| Inverter S. No. | Capacity | String 1: Voc | String 2: Voc | Remark |
| --- | --- | --- | --- | --- |
| 55000DSC251S1152 | 5KW | 805V |  |  |

Inverter Testing (AC) Side – Single / Three Phase

| Inverter S. No. | Capacity | R – Y/ P- N | Y – B | B - R | R – N | Y – N | B - N | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 55000DSC251S1152 | 5KW | 415V | 415V | 415V | 230V | 230V | 230V | -- |

ACDB & Meter Panel Testing – Single / Three Phase

|  | R – Y/ P-N | Y – B | B – R | R – N | Y – N | B - N | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ACDB I/C (V) | 415V | 415V | 415V | 230V | 230V | 230V | - |
| ACDB O/G (V) | 415V | 415V | 415V | 230V | 230V | 230V | - |

Earthing Pit Details: Nos. of Earth Pit 3 Nos.

|  | Earthing AC | Earthing DC | Earthing LA | Remark |
| --- | --- | --- | --- | --- |
| Earth Test Value (Ohm) | 5.5 Ohms | 5.2 Ohms | 5.8 Ohms |  |

Date: 27.05.2025

Site Engineer

Sign …………………………